## 1. Intro - Start Here
Venturi Meter - Gas Flow Calculations - S.I. Units
Workbook Contents
| Click on tabs at the bottom of the screen to access the following: |  | NOTE: The cells containing formulas are locked (protected) to avoid the
possibility of inadvertently typing over any of the formulas. You may,
|  | Tab 1. Contents (current tab) | however, adjust the number of decimal places for any of the cells.
Tab 2. Gas Selection/Gas Properties
|  | Tab 3. Calculate Flow Rate - ISO 5167 | Notes on the use of these worksheets:
|  | Tab 4. Calculate Required Throat Diameter - ISO 5167 | 1. The Gas Properties worksheet should be used first to either i) select a gas from a
dropdown list and enter the gas temperature and pressure in the pipe or else ii) enter
|  | Tab 5. Calculate Pressure Difference - ISO 5167 | the viscosity, ratio of specific heats, critical temperature and critical pressure of some
other gas along with its temperature and pressure in the pipe.
Tab 6. Calculate Flow Rate for User Specified Value of C
2. If a gas is selected from the dropdown list, then the viscosity, ratio of specific heats,
|  | Tab 7. Calc. Throat Diam. for User Specified Value of C | critical temperature, and critical pressure of that gas will be shown on the worksheet and
will be used for calculations in all of the other worksheets.
Tab 8. Calc. Pressure Diff. for User Specified Value of C
3. For a gas not on the dropdown list, the user entered properties will be used in the
other worksheets.
4. The compressibility factor is calculated using the Redlich-Kwong equation of state.
Note that in order to get accurate results with Redlich-Kwong equation calculations,
P/Pc should be less than T/(2Tc).
| Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved. |  | 5. Tabs 3, 4, and 5 make calculations for flow through Venturi meters meeting one
of the three ISO 5167 standard configurations.
Other requirements for use of the ISO 5167-4:2003
equations are summarized on the worksheets.
6. Tabs 6, 7, and 8 make calculations with a user specified value for the discharge
coefficient, C. These tabs are available to use with Venturi meters for
which tabs 3-5 are not useable.

## 2. Gas Properties
| Selection of Gas and Setting/Calculating the Gas | [5 empty] | 1. For calculations with one of the 21 gases listed in the table below, select the appropriate gas
| property values for use in the other Worksheets | [5 empty] | from the dropdown list in cell D12 and enter the gas temperature and pressure in cells D14
and D15. The gas viscosity, molecular weight, critical temperature, critical pressure, and
specific heat ratio will be shown below on this worksheet and those values will be used
FLUID VISCOSITY |  | Either (i) select a Gas and enter its temperature and pressure in the indicated |  |  |  |  | for calculations in all of the other worksheets.
yellow cells below, so that its viscosity will be calculated and used, or else
|  | (ii) enter the gas viscosity in the yellow cell D30 below and that value will be used. |  |  |  |  | 2. For calculations with some other gas, not listed in the table below, the user must enter
values for the gas viscosity, molecular weight, critical temperature, critical pressure, and
|  | Select a Gas and Enter Temperature |  | (Enter Values in yellow cells only) |  |  | specific heat ratio in the indicated yellow cells in column D. Those user entered property
values will be used for calculations in all of the other worksheets. The gas temperature
|  | Click at right to Select Gas | Methane |  |  |  | and pressure must be entered in the yellow cells, D14 and D15.
|  | Temperature Range (oC): | -183 to 727 | NOTE: For accurate calculation of Z with
|  | Gas Temperature (oC): | 27 | the Redlich-Kwong equation, the reduced |  |  |  | 3. For either a gas selected from the dropdown list or user entered gas properties,
|  | Gas Pressure in Pipe (kPa abs): | 690 | pressure should be less than half of the |  |  |  | the gas compressibility factor is calculated with the Redlich-Kwong Equation.
|  | Gas Viscosity (Pa-s): | 1.1254e-05 | reduced temperature. That is: P/Pc < T/(2Tc) |  |  |  | For accurate results P and T values should be such that P/Pc < T/(2Tc).
|  | Check on Gas Temperature and Gas Pressure Values entered above: | [6 empty] | The sources for the values in this table are: |  |  | Viscosity: | Table 2-138 in Perry's Chemical Engineers' Handbook, 9th Ed.
|  | Is P/Pc < T/(2Tc)? | YES |  | P/Pc = | 0.15003 |  |  |  |  | Mol Wt, Tc & Pc: |  | Table 2-106 in Perry's Chemical Engineers' Handbook, 9th Ed.
[5 empty] | T/2Tc = | 1.2769 |  |  |  |  | Specific Heat Ratio, k: |  | Table E7.3 in Piping Handbook, 7th Ed.
The entered values for T and P above are ok.
Excel Vlookup results based on selected fluid:
|  | NOTE: If you want to use a gas from the menu | [7 empty] | -183 to 727 | 5.2546e-07 | 0.59006 | 105.67 | 0 | 16.042 | 190.564 | 4599 | 1.32
|  | above, then the yellow cell, D30, below must be blank. | [6 empty] | Calculations: | 1.1254e-05 | Variables for Viscosity Calculations:
|  | Use the viscosity value above, OR | [7 empty] | Range, ºC | c1 | c2 | c3 | c4 | Mol. Weight | Tc, K | Pc, kPa | Cp/Cv
[9 empty] | Acetylene | -80.7 to 327 | 1.2025e-06 | 0.4952 | 291.4 |  | 26.037 | 308.3 | 6138 | 1.3
|  | Enter a Gas Viscosity Obtained Elsewhere | [6 empty] | Air | -193 to 1727 | 1.425e-06 | 0.5039 | 105.3 |  | 28.96 | 132.45 | 3774 | 1.4
[9 empty] | Ammonia | -78 to 727 | 4.1855e-08 | 0.9806 | 30.8 |  | 17.031 | 405.65 | 11280 | 1.32
|  | Gas Viscosity (Pa-s): | [6 empty] | Argon | -189 to 3000 | 9.2121e-07 | 0.60529 | 83.24 |  | 39.948 | 150.86 | 4898 | 1.67
[9 empty] | Butane | -138 to 727 | 3.4387e-08 | 0.94604 |  |  | 58.122 | 425.12 | 3796 | 1.11
|  | Gas Viscosity Result: | 1.1254e-05 | Pa-s | (from menu selection) |  |  |  | Carbon Dioxide | -78 to 1227 | 2.148e-06 | 0.46 | 290 |  | 44.01 | 304.21 | 7383 | 1.3
|  | (This is the viscosity value that will be used in all of the other worksheets.) | [6 empty] | Carbon Monoxide | -205 to 977 | 1.1127e-06 | 0.5338 | 94.7 |  | 28.01 | 132.92 | 3499 | 1.4
[9 empty] | Chlorine | -73 to 727 | 2.6e-07 | 0.7423 | 98.3 |  | 70.906 | 417.15 | 7710 | 1.33
MOLECULAR Wt. |  | Mol. Wt. from above menu selection: | [6 empty] | Ethane | -183 to 727 | 2.5906e-07 | 0.67988 | 98.902 |  | 30.069 | 305.32 | 4872 | 1.22
|  | 16.042 | [6 empty] | Ethylene | -104 to 727 | 2.0789e-06 | 0.4163 | 352.7 |  | 28.053 | 282.34 | 5041 | 1.22
[9 empty] | Helium | -253 to 1727 | 3.253e-07 | 0.7162 | -9.6 | 107 | 4.003 | 5.2 | 227.5 | 1.67
|  | NOTE: If you want to use a gas from the menu | [6 empty] | Hydrogen | -259 to 2727 | 1.797e-07 | 0.685 | -0.59 | 140 | 2.016 | 33.19 | 1313 | 1.41
|  | above, then the yellow cell, D45, below must be blank. | [6 empty] | Hydrogen Chloride | -73 to 727 | 4.924e-07 | 0.6702 | 157.7 |  | 36.461 | 324.65 | 8310 | 1.41
[9 empty] | Hydrogen Sulfide | -23 to 207 | 3.9314e-08 | 1.0134 |  |  | 34.081 | 373.53 | 8963 | 1.3
|  | Use the Mol. Wt. value above, OR | [6 empty] | Methane | -183 to 727 | 5.2546e-07 | 0.59006 | 105.67 |  | 16.042 | 190.564 | 4599 | 1.32
[9 empty] | Nitric Oxide | -163 to 1227 | 6.5592e-07 | 0.6081 | 54.714 |  | 30.006 | 180.15 | 6480 | 1.4
|  | Enter a Gas Mol. Wt. Obtained Elsewhere | [6 empty] | Nitrogen | -210 to 1697 | 1.467e-06 | 0.5123 | 125.4 |  | 28.013 | 126.2 | 3400 | 1.41
[9 empty] | Oxygen | -219 to 1227 | 1.101e-06 | 0.5634 | 96.3 |  | 31.999 | 154.58 | 5043 | 1.4
|  | Gas Molecular Weight: | [6 empty] | Propane | -188 to 727 | 4.9054e-08 | 0.90125 |  |  | 44.096 | 369.83 | 4248 | 1.15
[9 empty] | Propylene | -185 to 727 | 7.3919e-07 | 0.5423 | 263.73 |  | 42.08 | 364.85 | 4600 | 1.14
|  | Molecular Weight Result: | 16.042 |  | (from menu selection) |  |  |  | Sulfur Dioxide | -75 to 727 | 6.863e-07 | 0.6112 | 217 |  | 64.064 | 430.75 | 7884 | 1.26
(This is the Molecular Weight that will be used in all of the other worksheets.)
CRITICAL TEMP. |  | Critical Temperature from above menu selection: | [6 empty] | Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved.
|  | 190.564 | K
NOTE: If you want to use a gas from the menu
above, then the yellow cell, D60, below must be blank.
Use the Critical Temperature value above, OR
Enter a Critical Temperature Obtained Elsewhere
Critical Temperature (K):
|  | Critical Temp. Result: | 190.564 | K | (from menu selection)
(This is the Critical Temperature that will be used in all of the other worksheets.)
CRITICAL PRESSURE |  | Critical Pressure from above menu selection:
|  | 4599 | kPa
NOTE: If you want to use a gas from the menu
above, then the yellow cell, D75, below must be blank.
Use the Critical Pressure value above, OR
Enter a Critical Pressure Obtained Elsewhere
Critical Pressure (kPa):
|  | Critical Pressure Result: | 4599 | kPa | (from menu selection)
(This is the Critical Pressure that will be used in all of the other worksheets.)
SPEC. HEAT RATIO |  | Spec. Heat Ratio from above menu selection:
1.32
NOTE: If you want to use a gas from the menu
above, then the yellow cell, D90, below must be blank.
Use the Specific Heat Ratio above, OR
Enter a Spec. Heat Ratio Obtained Elsewhere
Spec. Heat Ratio:
|  | Spec. Heat Ratio Result: | 1.32 |  | (from menu selection)
|  | (This is the Specific Heat Ratio that will be used in all of the other worksheets.) | [6 empty] | For the Redlich-Kwong Equation of State (used to calculate the compressibility factor, Z) see:
Handbook of Chemical Engineering Calculations, 4th Ed., Section 1.4, Redlich-Kwong Equation of State
COMPRESSIBILITY FACTOR |  | Calculation of Compressibility Factor of the Gas using the Redlich-Kwong Equation of State:
|  | (Note that P/Pc must be less than T/2Tc for accurate Redlich-Kwong Equation calculations.) | [6 empty] | The Redlich-Kwong
Equation of State:
Where:
|  | Is P/Pc < T/(2Tc) ? | YES | If this answer is "NO", change P and/or T |  |  |  |  | Z = Compressibility Factor
|  |  |  | in cell(s) D14 and/or D15 above. |  |  |  |  | T = Gas temperature, K
P = Gas pressure, atm
|  | Reduced Temperature, TR = | 1.5751 | Equation Constant, r = |  | 0.00017 |  |  | Tc = critical temperature of gas, K
|  | Reduced Pressure, PR = | 0.15003 | Equation Constant, q = |  | -0.012278 |  |  | Pc = critical pressure of gas, atm |  |  | Subject to: P/Pc < T/(2Tc)
|  | Equation Constant, A2 = | 0.020599 | Equation Constant, f = |  | -0.32106
|  | Equation Constant, B = | 0.0082529 | Equation Constant, g = |  | -0.070151
|  |  |  | calculated value of C = |  | 4.6284e-06 |  |  | The compressibility factor is calculated as described at: www.polymath-software.com/ASEE2007/PDF1.pdf.
It is calculated as the maximum real root of the equation: Z3 - Z2 - qZ - r = 0, where r = A2B and
|  |  |  | Z = | 0.98774 |  |  |  | q = B2 + B - A2, A2 = 0.42747 PR/TR2.5 and B = 0.08664 PR/TR.
[5 empty] | Z1 = |  |  |  | To find the maximum real root, first the parameter C is calculated, where C = (f/3)3 + (g/2)2, f = (-3q - 1)/3
|  | Equation Constant, f = |  |  | Z2 = |  |  |  | and g = (-27r - 9q - 2)/27. |  | If C > 0, there is one real root, Z = (-g/2 + C1/2)1/3 + (-g/2 - C1/2)1/3 + 1/3.
Z3 =
If C < 0, then there are three real roots, given by: Zk = 2(-f/3)1/2cos[(f/3) + 2p(k-1)/3] + 1/3, k = 1,2,3
with f = cos-1{[(g2/4)/((-f3)/27)]1/2}
Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved.
********************************** WORKSPACE ***************************************************************************************************************************
lbm
slugs

## 3. Flow Rate - ISO 5167
| Gas Flow/Venturi Meter Calculations - Flow Rate - S.I. Units | [6 empty] | References and Equations
For Venturi Meters Meeting ISO 5167-4:2003 Requirements
For background and descriptive information about Venturi flow meters see:
INPUTS | User Inputs: |  |  | Enter values in yellow cells only. |  |  | Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 8.8.4, Flow Measurements
Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 10.1.12, Differential Pressure Flowmeters
| Pipe Diameter, D = | 150 | mm
| (See link at right for std. pipe size table) |  |  | Measured Pressure |  |  | For a table with standard pipe size information, see:
|  |  |  | Difference, P1 - P2 = | 6.9 | kPa | Piping Handbook, 7th Ed., Table E2.1M - S.I. units
| Throat Diameter, d = | 50 | mm
| Elevation diff. between pipe centerline at press. taps, z1 - z2 = |  |  |  | 0 | mm
(Note that z1 - z2 = 0 for a horizontal meter)
Click on the green cell below and then on the arrow to the right of it and use the
| drop down list to specify the type of |  |  | as cast
ISO 5167 standard converging Venturi section being used.
CALCULATIONS | Calculations:
| Pipe Diameter, D = | 0.15 | m | Throat Diameter, d = | 0.05 | m
| Pipe Area, A1 = | 0.017671 | m2 | Throat Area, A2 = | 0.0019635 | m2 | The equation for gas flow rate through a Venturi meter (horizontal, inclined or vertical) is:
| Diameter Ratio, b = | 0.33333 |  | Measured Pressure |  |  | (Adapted from: |  | Perry's Chemical Engineers' Handbook, 9th Ed, Equation 10-25 )
| Discharge Coeff., C = | 0.984 |  | Difference, P1 - P2 = | 6900 | Pa
| Fluid Density, r = | 4.4827 | kg/m3 | Pressure Ratio, P2/P1 = | 0.99
| Expansion Factor, Y = | 0.99421 |  | Pipe Flow Rate, Q = | 0.10715 | m3/s
| Ideal Gas Law |  |  | Pipe Velocity, V = | 6.0635 | m/s | Where: Q = flow rate through the pipe and through the meter, m3/s
| Constant, R = | 8.3145 | kN-m/kgmole-K |  |  |  | C = discharge coefficient, dimensionless
|  |  |  | Reynolds No., Re = | 362267.0573 |  | A2 = Venturi throat area, m2
|  |  |  | (in pipe) |  |  | P1 = absolute pressure in the pipe at upstream pressure tap, Pa
P1 - P2 = pressure difference between upstream and downstream pressure taps, Pa
b = d/D = throat diam./pipe diam., dimensionless
RESULTS | Results: | [5 empty] | Z = compressibility factor of the gas at P1, T1
R = Ideal Gas Law Constant = 8.3145 kN-m/kgmole-K
| Pipe Flow Rate, Q = |  |  | 0.10715 | m3/s |  | MW = molecular weight of gas
| Uncertainty of | [5 empty] | T1 = upstream absolute temperature in the pipe, K
| Calculated Discharge Coefficient, C ( + ): |  |  | 0.7% |  |  | Y = Expansion Factor - see equation for Y below
| (from ISO 5167-4:2003 section 5.7) | [5 empty] | g = acceleration due to gravity = 9.81 m/s2
| Are all of the conditions for use of ISO 5167-4:2003 equations met? |  |  |  | yes |  | z1 - z2 = difference between elevation of pipe centerline at pressure tap 1 and pressure tap 2, m
( See the details of the check on the required conditions below. )
LIMITS - ISO 5167-4:2003 | Check on the Conditions Required for Use of ISO 5167-4:2003 Discharge Coefficient:
| Dmin = | 100 | mm | Dmax = | 800 | mm
| bmin = | 0.3 |  | bmax = | 0.75
| Remin = | 200000 |  | Remax = | 2000000 |  | Y = Expansion Factor, dimensionless
k = isentropic constant [ specific heat ratio (Cp/Cv)], dimensionless
| Is D > Dmin ? | yes |  | Is D < Dmax ? | yes |  | t = Pressure Ratio, P2/P1, dimensionless
b = d/D = throat diam./pipe diam., dimensionless
| Is b > bmin ? | yes |  | Is b < bmax ? | yes
| Is Re > Remin ? | yes |  | Is Re < Remax ? | yes
The source for the discharge coefficient values and the pipe/meter/flow conditions required for their use is:
If the conditions for use of ISO 5167-4-2003 equations are not met and the flow
| and/or pipe/meter configuration cannot be adjusted to meet these conditions | [5 empty] | International Organization for Standardization (ISO), Measurement of fluid flow by means of pressure
| then Tabs 6-8 may be used for calculations with a user specified value for the | [5 empty] | differential devices inserted in circular cross-section conduits running full - Part 4: Venturi Meters
| discharge coefficient, C. | [5 empty] | Reference Number: ISO 5167-4:2003
Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved.
psi
in. Hg
as cast
machined
rough welded sheet iron

## 4. Throat Diameter - ISO 5167
| Gas Flow/Venturi Meter Calculations - Throat Diam. - S.I. Units | [6 empty] | References and Equations
For Venturi Meters Meeting ISO 5167-4:2003 Requirements
For background and descriptive information about Venturi flow meters see:
INPUTS | User Inputs: |  |  | Enter values in yellow cells only. |  |  | Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 8.8.4, Flow Measurements
Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 10.1.12, Differential Pressure Flowmeters
| Pipe Diameter, D = | 100 | mm | Pipe Flow Rate, Q = | 0.04 | m3/s
| (See link at right for std pipe size table) |  |  | Assumed value of |  |  | For a table with standard pipe size information, see:
| Press. Diff., P1 - P2 = | 2 | kPa | Throat Diam., d = | 41.3704 | mm | Piping Handbook, 7th Ed., Table E2.1M - S.I. units
| (target value) |  |  | (needed to start iterative calculation)
| Elevation diff. between pipe centerline at press. taps, z1 - z2 = |  |  |  | 0 | mm
(Note that z1 - z2 = 0 for a horizontal meter)
Click on the green cell below and then on the arrow to the right of it and use the
| drop down list to specify the type of |  |  | as cast
ISO 5167 standard converging Venturi section being used.
CALCULATIONS | Calculations:
| Pipe Diameter, D = | 0.1 | m | Throat Diameter, d = | 0.04137 | m
| Pipe Area, A1 = | 0.007854 | m2 | Throat Area, A2 = | 0.0013442 | m2 | The equation for gas pressure difference through a Venturi meter (horizontal, inclined or vertical) is:
| Diameter Ratio, b = | 0.4137 |  | Pressure Ratio, P2/P1 = | 0.9971 |  | (Adapted from: |  | Perry's Chemical Engineers' Handbook, 9th Ed, Equation 10-25 )
| Discharge Coeff., C = | 0.984 |  | Pipe Velocity, V = | 5.093 | m/s
| Fluid Density, r = | 4.4904 | kg/m3 | Reynolds No., Re = | 203205.7859
Calculated Pressure
| Expansion Factor, Y = | 0.99829 |  | Difference, P1 - P2 = | 2000 | Pa
| Ideal Gas Law |  | Difference between target and |  |  |  | Where: Q = flow rate through the pipe and through the meter, m3/s
| Constant, R = | 8.3145 | calculated values of P1 - P2 = |  | 4.735e-06 | Pa | C = discharge coefficient, dimensionless
|  | kN-m/kgmole-K |  |  |  |  | A2 = Venturi throat area, m2
P1 = absolute pressure in the pipe at upstream pressure tap, Pa
P1 - P2 = pressure difference between upstream and downstream pressure taps, Pa
| NOTE: You must use Excel's "Goal Seek" to find the throat diameter as follows: Place the | [5 empty] | b = d/D = throat diam./pipe diam., dimensionless
| cursor on cell G32 and click on "Goal Seek" (in the "Tools" menu of older versions and under | [5 empty] | Z = compressibility factor of the gas at P1, T1
| "Data - What If Analysis" in newer versions of Excel). Enter values G32 to "Set cell:", | [5 empty] | R = Ideal Gas Law Constant = 8.3145 kN-m/kgmole-K
| 0 to "To value:", G11 to "By changing cell:", and click on "OK". The calculated value of d will | [5 empty] | MW = molecular weight of gas
| appear in cell G11 and below in cell F45. The yellow cell G11 needs an initial estimate | [5 empty] | T1 = upstream absolute temperature in the pipe, K
| of d to start the iterative process. | [5 empty] | Y = Expansion Factor - see equation for Y below
g = acceleration due to gravity = 9.81 m/s2
RESULTS | Results: | [5 empty] | z1 - z2 = difference between elevation of pipe centerline at pressure tap 1 and pressure tap 2, mm
| Throat Diameter Needed, d = |  |  | 41.3704 | mm
Uncertainty of
| Calculated Discharge Coefficient, C ( + ): |  |  | 0.7%
(from ISO 5167-4:2003 section 5.7)
| Are all of the conditions for use of ISO 5167-4:2003 equations met? |  |  |  | yes
(See the details of the check on the required conditions below.)
Y = Expansion Factor, dimensionless
k = isentropic constant [ specific heat ratio (Cp/Cv)], dimensionless
LIMITS - ISO 5167-4:2003 | Check on the Conditions Required for Use of ISO 5167-4:2003 Discharge Coefficient: | [5 empty] | t = Pressure Ratio, P2/P1, dimensionless
b = d/D = throat diam./pipe diam., dimensionless
| Dmin = | 100 | mm | Dmax = | 800 | mm
| bmin = | 0.3 |  | bmax = | 0.75
| Remin = | 200000 |  | Remax = | 2000000
| Is D > Dmin ? | yes |  | Is D < Dmax ? | yes
The source for the discharge coefficient values and the pipe/meter/flow conditions required for their use is:
| Is b > bmin ? | yes |  | Is b < bmax ? | yes
International Organization for Standardization (ISO), Measurement of fluid flow by means of pressure
| Is Re > Remin ? | yes |  | Is Re < Remax ? | yes |  | differential devices inserted in circular cross-section conduits running full - Part 4: Venturi Meters
Reference Number: ISO 5167-4:2003
If the conditions for use of ISO 5167-4-2003 equations are not met and the flow
and/or pipe/meter configuration cannot be adjusted to meet these conditions
then Tabs 6-8 may be used for calculations with a user specified value for the
discharge coefficient, C.
Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved.
psi
in. Hg
as cast
machined
rough welded sheet iron

## 5. Pressure Diff. - ISO 5167
| Gas Flow/Venturi Meter Calculations - Pressure Diff. - S.I. Units | [6 empty] | References and Equations
For Venturi Meters Meeting ISO 5167-4:2003 Requirements
For background and descriptive information about Venturi flow meters see:
INPUTS | User Inputs: |  |  | Enter values in yellow cells only. |  |  | Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 8.8.4, Flow Measurements
Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 10.1.12, Differential Pressure Flowmeters
| Pipe Diameter, D = | 100 | mm | Pipe Flow Rate, Q = | 0.06 | m3/s
| (See link at right for std pipe size table) |  |  | Assumed value of |  |  | For a table with standard pipe size information, see:
| Throat Diam., d = | 30 | mm | Press. Diff., P1 - P2 = | 17.0557 | kPa | Piping Handbook, 7th Ed., Table E2.1M - S.I. units
(needed to start iterative calculation)
| Elevation diff. between pipe centerline at press. taps, z1 - z2 = |  |  |  | 0 | mm
(Note that z1 - z2 = 0 for a horizontal meter)
Click on the green cell below and then on the arrow to the right of it and use the
| drop down list to specify the type of |  |  | as cast
ISO 5167 standard converging Venturi section being used.
CALCULATIONS | Calculations:
| Pipe Diameter, D = | 0.1 | m | Throat Diameter, d = | 0.03 | m
| Pipe Area, A1 = | 0.007854 | m2 | Throat Area, A2 = | 0.00070686 | m2
| Diameter Ratio, b = | 0.3 |  | Pressure Ratio, P2/P1 = | 0.97528
| Discharge Coeff., C = | 0.984 |  | Pipe Velocity, V = | 7.6394 | m/s | The equation for gas pressure difference through a Venturi meter (horizontal, inclined or vertical) is:
| Fluid Density, r = | 4.4904 | kg/m3 | Reynolds No., Re = | 304808.6788 |  | (Adapted from: |  | Perry's Chemical Engineers' Handbook, 9th Ed, Equation 10-25 )
Calculated Pressure
| Expansion Factor, Y = | 0.98572 |  | Difference, P1 - P2 = | 17055.6807 | Pa
| Ideal Gas Law |  | Difference between target and
| Constant, R = | 8.3145 | calculated values of P1 - P2 = |  | -4.2564e-09 | Pa
|  | kN-m/kgmole-K |  |  |  |  | Where: Q = flow rate through the pipe and through the meter, m3/s
C = discharge coefficient, dimensionless
A2 = Venturi throat area, m2
| NOTE: You must use Excel's "Goal Seek" to find the pressure difference as follows: Place the | [5 empty] | P1 = absolute pressure in the pipe at upstream pressure tap, Pa
| cursor on cell G30 and click on "Goal Seek" (in the "Tools" menu of older versions and under | [5 empty] | P1 - P2 = pressure difference between upstream and downstream pressure taps, Pa
| "Data - What If Analysis" in newer versions of Excel). Enter values G30 to "Set cell:", | [5 empty] | b = d/D = throat diam./pipe diam., dimensionless
| 0 to "To value:", G11 to "By changing cell:", and click on "OK". The calculated value of P1 - P2 will | [5 empty] | Z = compressibility factor of the gas at P1, T1
| appear in cell G11 and below in cell F43. The yellow cell G11 needs an initial estimate | [5 empty] | R = Ideal Gas Law Constant = 8.3145 kN-m/kgmole-K
| of P1 - P2 to start the iterative process. | [5 empty] | MW = molecular weight of gas
T1 = upstream absolute temperature in the pipe, K
RESULTS | Results: | [5 empty] | Y = Expansion Factor - see equation for Y below
g = acceleration due to gravity = 9.81 m/s2
| Pressure Difference, P1 - P2 = |  |  | 17.0557 | kPa |  | z1 - z2 = difference between elevation of pipe centerline at pressure tap 1 and pressure tap 2, mm
Uncertainty of
| Calculated Discharge Coefficient, C ( + ): |  |  | 0.7%
(from ISO 5167-4:2003 section 5.7)
| Are all of the conditions for use of ISO 5167-4:2003 equations met? |  |  |  | yes
(See the details of the check on the required conditions below.)
LIMITS - ISO 5167-4:2003 | Check on the Conditions Required for Use of ISO 5167-4:2003 Discharge Coefficient: | [5 empty] | Y = Expansion Factor, dimensionless
k = isentropic constant [ specific heat ratio (Cp/Cv)], dimensionless
| Dmin = | 100 | mm | Dmax = | 800 | mm | t = Pressure Ratio, P2/P1, dimensionless
| bmin = | 0.3 |  | bmax = | 0.75 |  | b = d/D = throat diam./pipe diam., dimensionless
| Remin = | 200000 |  | Remax = | 2000000
| Is D > Dmin ? | yes |  | Is D < Dmax ? | yes
| Is b > bmin ? | yes |  | Is b < bmax ? | yes
The source for the discharge coefficient values and the pipe/meter/flow conditions required for their use is:
| Is Re > Remin ? | yes |  | Is Re < Remax ? | yes
International Organization for Standardization (ISO), Measurement of fluid flow by means of pressure
differential devices inserted in circular cross-section conduits running full - Part 4: Venturi Meters
Reference Number: ISO 5167-4:2003
If the conditions for use of ISO 5167-4-2003 equations are not met and the flow
and/or pipe/meter configuration cannot be adjusted to meet these conditions
then Tabs 6-8 may be used for calculations with a user specified value for the
discharge coefficient, C.
Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved.
as cast
machined
rough welded sheet iron

## 6. Flow Rate - Specified C
| Gas Flow/Venturi Meter Calculations - Flow Rate - S.I. Units | [6 empty] | References and Equations
User Specified Discharge Coefficient, C
For background and descriptive information about Venturi flow meters see:
INPUTS | User Inputs: |  |  | Enter values in yellow cells only. |  |  | Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 8.8.4, Flow Measurements
Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 10.1.12, Differential Pressure Flowmeters
| Pipe Diameter, D = | 150 | mm | Throat Diameter, d = | 50 | mm
| (See link at right for std pipe size table) | [5 empty] | For a table with standard pipe size information, see:
|  |  |  | Measured Pressure |  |  | Piping Handbook, 7th Ed., Table E2.1M - S.I. units
| Discharge Coeff., C = | 0.984 |  | Difference, P1 - P2 = | 6.9 | kPa
| Elevation diff. between pipe centerline at press. taps, z1 - z2 = |  |  |  | 0 | in
(Note that z1 - z2 = 0 for a horizontal meter)
CALCULATIONS | Calculations:
| Pipe Diameter, D = | 0.15 | m | Throat Diameter, d = | 0.05 | m
| Pipe Area, A1 = | 0.017671 | m2 | Throat Area, A2 = | 0.0019635 | m2
| Diameter Ratio, b = | 0.33333 |  | Measured Pressure
|  |  |  | Difference, P1 - P2 = | 6900 | Pa
| Fluid Density, r = | 4.4904 | kg/m3 | Pressure Ratio, P2/P1 = | 0.99 |  | The equation for gas flow rate through a Venturi meter (horizontal, inclined or vertical) is:
[7 empty] | (Adapted from: |  | Perry's Chemical Engineers' Handbook, 9th Ed, Equation 10-25 )
| Expansion Factor, Y = | 0.99421 |  | Pipe Flow Rate, Q = | 0.10715 | m3/s
| Ideal Gas Law |  |  | Pipe Velocity, V = | 6.0635 | m/s
| Constant, R = | 8.3145 | kN-m/kgmole-K
|  |  |  | Reynolds No., Re = | 362894.673
|  |  |  | (in pipe) |  |  | Where: Q = flow rate through the pipe and through the meter, m3/s
C = discharge coefficient, dimensionless
A2 = Venturi throat area, m2
P1 = absolute pressure in the pipe at upstream pressure tap, Pa
P1 - P2 = pressure difference between upstream and downstream pressure taps, Pa
| Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved. | [5 empty] | b = d/D = throat diam./pipe diam., dimensionless
Z = compressibility factor of the gas at P1, T1
R = Ideal Gas Law Constant = 8.3145 kN-m/kgmole-K
MW = molecular weight of gas
T1 = upstream absolute temperature in the pipe, K
Y = Expansion Factor - see equation for Y below
g = acceleration due to gravity = 9.81 m/s2
z1 - z2 = difference between elevation of pipe centerline at pressure tap 1 and pressure tap 2, m
Y = Expansion Factor, dimensionless
k = isentropic constant [ specific heat ratio (Cp/Cv)], dimensionless
t = Pressure Ratio, P2/P1, dimensionless
b = d/D = throat diam./pipe diam., dimensionless
psi
in. Hg

## 7. Throat Diam - Specified C
| Gas Flow/Venturi Meter Calculations - Throat Diam. - S.I. Units | [6 empty] | References and Equations
User Specified Discharge Coefficient, C
For background and descriptive information about Venturi flow meters see:
INPUTS | User Inputs: |  |  | Enter values in yellow cells only. |  |  | Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 8.8.4, Flow Measurements
Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 10.1.12, Differential Pressure Flowmeters
| Pipe Diameter, D = | 100 | mm | Pipe Flow Rate, Q = | 0.04 | m3/s
| (See link at right for std pipe size table) |  |  | Assumed value of |  |  | For a table with standard pipe size information, see:
| Press. Diff., P1 - P2 = | 2 | kPa | Throat Diam., d = | 41.3704 | mm | Piping Handbook, 7th Ed., Table E2.1M - S.I. units
| (target value) |  |  | (needed to start iterative calculation)
| Discharge Coeff., C = | 0.984
| Elevation diff. between pipe centerline at press. taps, z1 - z2 = |  |  |  | 0 | mm
(Note that z1 - z2 = 0 for a horizontal meter)
CALCULATIONS | Calculations:
| Pipe Diameter, D = | 0.1 | m | Throat Diameter, d = | 0.04137 | m
| Pipe Area, A1 = | 0.007854 | m2 | Throat Area, A2 = | 0.0013442 | m2
| Diameter Ratio, b = | 0.4137 |  | Pressure Ratio, P2/P1 = | 0.9971
|  |  |  | Pipe Velocity, V = | 5.093 | m/s
| Fluid Density, r = | 4.4904 | kg/m3 | Reynolds No., Re = | 203205.7859 |  | The equation for gas pressure difference through a Venturi meter (horizontal, inclined or vertical) is:
|  |  |  | Calculated Pressure |  |  | (Adapted from: |  | Perry's Chemical Engineers' Handbook, 9th Ed, Equation 10-25 )
| Expansion Factor, Y = | 0.99829 |  | Difference, P1 - P2 = | 2000 | Pa
| Ideal Gas Law |  | Difference between target and
| Constant, R = | 8.3145 | calculated values of P1 - P2 = |  | -4.5743e-05 | lbf/ft2
kN-m/kgmole-K
Where: Q = flow rate through the pipe and through the meter, m3/s
C = discharge coefficient, dimensionless
RESULTS | NOTE: You must use Excel's "Goal Seek" to find the throat diameter as follows: Place the | [5 empty] | A2 = Venturi throat area, m2
| cursor on cell G29 and click on "Goal Seek" (in the "Tools" menu of older versions and under | [5 empty] | P1 = absolute pressure in the pipe at upstream pressure tap, Pa
| "Data - What If Analysis" in newer versions of Excel). Enter values G29 to "Set cell:", | [5 empty] | P1 - P2 = pressure difference between upstream and downstream pressure taps, Pa
| 0 to "To value:", and G11 to "By changing cell:", then click on "OK". The calculated value of d | [5 empty] | b = d/D = throat diam./pipe diam., dimensionless
| will appear in cell G11 and below in cell F41. The yellow cell G11 needs an initial estimate | [5 empty] | Z = compressibility factor of the gas at P1, T1
| of d to start the iterative process. | [5 empty] | R = Ideal Gas Law Constant = 8.3145 kN-m/kgmole-K
MW = molecular weight of gas
T1 = upstream absolute temperature in the pipe, K
| Throat Diameter Needed, d = |  |  | 41.3704 | in |  | Y = Expansion Factor - see equation for Y below
g = acceleration due to gravity = 9.81 m/s2
z1 - z2 = difference between elevation of pipe centerline at pressure tap 1 and pressure tap 2, m
Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved.
Y = Expansion Factor, dimensionless
k = isentropic constant [ specific heat ratio (Cp/Cv)], dimensionless
t = Pressure Ratio, P2/P1, dimensionless
b = d/D = throat diam./pipe diam., dimensionless

## 8. Press Diff - Specified C
| Gas Flow/Venturi Meter Calculations - Pressure Diff. - S.I. Units | [6 empty] | References and Equations
User Specified Discharge Coefficient, C
For background and descriptive information about Venturi flow meters see:
INPUTS | User Inputs: |  |  | Enter values in yellow cells only. |  |  | Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 8.8.4, Flow Measurements
Perry's Chemical Engineers' Handbook, 9th Ed, Sec. 10.1.12, Differential Pressure Flowmeters
| Pipe Diameter, D = | 100 | mm | Pipe Flow Rate, Q = | 0.06 | m3/s
| (See link at right for std pipe size table) | [5 empty] | For a table with standard pipe size information, see:
| Throat Diam., d = | 30 | mm | Assumed value of |  |  | Piping Handbook, 7th Ed., Table E2.1M - S.I. units
|  |  |  | Press. Diff., P1 - P2 = | 17.0557 | kPa
| Discharge Coeff., C = | 0.984 |  | (needed to start iterative calculation)
| Elevation diff. between pipe centerline at press. taps, z1 - z2 = |  |  |  | 0 | mm
(Note that z1 - z2 = 0 for a horizontal meter)
CALCULATIONS | Calculations:
| Pipe Diameter, D = | 0.1 | m | Throat Diameter, d = | 0.03 | m
| Pipe Area, A1 = | 0.007854 | m2 | Throat Area, A2 = | 0.00070686 | m2
| Diameter Ratio, b = | 0.3 |  | Pressure Ratio, P2/P1 = | 0.97528
|  |  |  | Pipe Velocity, V = | 7.6394 | ft/sec | The equation for gas pressure difference through a Venturi meter (horizontal, inclined or vertical) is:
| Fluid Density, r = | 4.4904 | kg/m3 | Reynolds No., Re = | 304808.6788 |  | (Adapted from: |  | Perry's Chemical Engineers' Handbook, 9th Ed, Equation 10-25 )
Calculated Pressure
| Expansion Factor, Y = | 0.98572 |  | Difference, P1 - P2 = | 17055.6807 | Pa
| Ideal Gas Law |  | Difference between target and
| Constant, R = | 8.3145 | calculated values of P1 - P2 = |  | -4.2564e-09 | Pa
|  | kN-m/kgmole-K |  |  |  |  | Where: Q = flow rate through the pipe and through the meter, m3/s
C = discharge coefficient, dimensionless
A2 = Venturi throat area, m2
RESULTS | NOTE: You must use Excel's "Goal Seek" to find the pressure difference as follows: Place the | [5 empty] | P1 = absolute pressure in the pipe at upstream pressure tap, Pa
| cursor on cell G30 and click on "Goal Seek" (in the "Tools" menu of older versions and under | [5 empty] | P1 - P2 = pressure difference between upstream and downstream pressure taps, Pa
| "Data - What If Analysis" in newer versions of Excel). Enter values G30 to "Set cell:", | [5 empty] | b = d/D = throat diam./pipe diam., dimensionless
| 0 to "To value:", and G12 to "By changing cell:", then click on "OK". The calculated value of P1 - P2 | [5 empty] | Z = compressibility factor of the gas at P1, T1
| will appear in cell G12 and below in cell F43. The yellow cell G12 needs an initial estimate | [5 empty] | R = Ideal Gas Law Constant = 8.3145 kN-m/kgmole-K
| of P1 - P2 to start the iterative process. | [5 empty] | MW = molecular weight of gas
T1 = upstream absolute temperature in the pipe, K
Y = Expansion Factor - see equation for Y below
| Pressure Difference, P1 - P2 = |  |  | 17.0557 | kPa |  | g = acceleration due to gravity = 9.81 m/s2
z1 - z2 = difference between elevation of pipe centerline at pressure tap 1 and pressure tap 2, m
Copyright © McGraw-Hill Global Education Holdings, LLC. All rights reserved.
Y = Expansion Factor, dimensionless
k = isentropic constant [ specific heat ratio (Cp/Cv)], dimensionless
t = Pressure Ratio, P2/P1, dimensionless
b = d/D = throat diam./pipe diam., dimensionless